	METERING PUMP DATA SHEET
1	PROJECT			JOB NO.
2	PURCHASER			ITEM NO.
3	SERVICE			QUANTITY
4	OPERATING CONDITIONS			PERFORMANCE
5	LIQUID			PUMP MODEL		KPV-121M-ST-S
6	PUMPING TEMP (℃)			PUMPING TEMP (℃)		0~100℃
7	AMBIENT TEMP (℃)			VISCOSITY (cP)		MAX 500
8	SPECIFIC GRAVITY			CAPACITY (mL/min)		MAX 85
9	VISCOSITY (cP)			DISCHARGE PRESS (bar)		MAX 225
10	CAPACITY (mL/min)			STROKE SPEED (SPM)		58
11	DISCHARGE PRESS (bar)			STROKE LENGTH (㎜)		15
12	SUCTION PRESS (bar)			PLUNGER DIA (㎜)		12
13	NPSH AVAILABLE (m)			NPSH REQUIRED (m)		3.5
14	LOCATION			BHP RATED (kW)		0.193
15	CONSTRUCTION			MATERIALS
16	PUMP TYPE		PLUNGER	HEAD		STS316
17	FEED NUMBER		SINGLE	PLUNGER		STS316+CQ
18	VALVE TYPE		CHECK BALL	CHECK BALL		STS316
19	VALVE NUMBER		DOUBLE	BALL GUIDE		STS316
20	CONNECTION TYPE		THREAD	BALL SEAT		STS316
21	SUCTION SIZE		Rc 1/4	GLAND PACKING		PTFE+ARAMID
22	DISCHARGE SIZE		Rc 1/4	VALVE GASKET		PTFE+PFA
23	CONTROL			DRIVE (MOTOR)
24	TYPE		MANUAL	TYPE		TEFC
25	METHOD		STROKE ADJUSTMENT	MANUFACTURER		SHINKANG
26	ADJUSTMENT RANGE		10~100%	OUTPUT (kW)		0.4
27	PAINTING COLOR			VOLTAGE/PHASE/HERTZ		220/380V / 3Ø / 60Hz
28	PUMP (Munsell No)		0.6PB 4.8/10.6	SPEED (RPM)		1720
29	MOTOR (Munsell No)		6.3G 8.2/0.4	INSULATION CLASS		F
30	LUBRICATION FLUID		GEAR BOX (GEAR OIL)	PROTECTION DEGREE		IP54
31	WEIGHTS (kg)		41	HUB SIZE		Ø22
32	ACCESSORIES			SPARE PARTS
33	□ RELIEF VALVE □ BACK PRESS VALVE			□ PLUNGER □ BALL SEAT
34	□ ACCUMULATOR(AIR CHAMBER)			□ CHECK BALL □ BALL GUIDE
35	□ PRESSURE GAUGE			□ GLAND PACKING □ VALVE GASKET
36	REMARKS:
37

CHEON-SEI IND.CO.,LTD.